Energy Management Control System (EMCS) and/or Direct Digital Control (DDC) System Requirements for New Facilities

- Provide building-level supervisory controllers based on Eglin’s existing Niagara 4.0 framework, matching the current Niagara 4.13 Enterprise Network Server (ENS) configuration. Building-level supervisory controllers shall include point-to-point (P2P), Secure Socket Layer (SSL), Web Server, and embedded Workbench (WB) capability. All control devices shall be fully programmable only through Niagara Workbench’s graphical block-based “Wire Sheet” programming environment. The use of any script-based, text-based, or proprietary programming methods (including but not limited to Script Programs, BQL logic, PX scripts, or vendor-specific code) is strictly prohibited. All programming shall be developed exclusively using block-based control logic components available within the Niagara 4.13 Workbench toolset. Each control sequence shall be visually represented, documented, and editable through Wire Sheet connections. The use of configurable or programmable controllers that require additional software tools, third-party applications, or manufacturer-specific licenses beyond standard Niagara Workbench shall not be acceptable. All control logic, graphics, and local controller backups shall reside within the building-level supervisory controller (JACE). JACE units shall be installed in the mechanical room.

- All graphics and points shall be duplicated within the existing Niagara 4.13 Framework ENS located in Building 696, which serves as the web server for the system. All trended points shall be transferred via P2P to the ENS for history trending and archival.

- Provide Niagara Workbench software matching the current version of the ENS Niagara Framework. All field controller software shall be issued by the contractor to the DDC shop upon completion of the project. Provide all necessary USB adapters for each type of DDC field controller, including factory installed unit controllers.

- The system shall allow Civil Engineer (CE) technicians to connect to all controllers using Niagara Workbench from Building 696 via the local area network (LAN) to perform all programming, backups, downloads, configurations, and maintenance functions as if directly connected to the device.

- All administrator level passwords for hardware and software shall be provided to the government, including full access to all controllers and Niagara Framework components. Provide a complete topology, hardware/software inventory, and configuration documentation. Leave the default factory Platform Username and Password.

- The Building Automation System (BAS) field controllers used on all projects shall be limited to the following manufacturers to maintain enterprise-wide system compatibility, standardization, cybersecurity compliance, and long-term maintainability: Johnson Controls Facility Explorer, Trane, and Honeywell. All controllers shall be fully programmable and support BACnet/IP (BACnet over Internet Protocol) communication. Controllers must be capable of direct integration with the existing Niagara JACE building automation platform without the use of proprietary gateways, drivers, or middleware. This requirement applies to all new construction, renovation, and system upgrade projects

- Provide a LAN drop within three feet of each building-level supervisory controller, including patch cabling between the LAN drop and the supervisory controller.

- When the BACnet communication bus leaves or enters a building, use fiber optic cabling and provide media converter pairs (e.g., between buildings or out to chillers), along with DB testing results.

- The BACnet communication bus shall be daisy-chained to the JACE. No additional switches or routers shall be used.

- The DDC shop shall be notified for pre-final and final inspection for acceptance of the project.

Energy Management Control System (EMCS) and/or Direct Digital Control (DDC) System Requirements for Existing Facility Remodels

- Modifications to an existing facility’s Control System (CS) must be fully compatible with the current system in that facility if the new controls are connected to an existing JACE. Whenever possible, the same brand of controls should be used. If a new JACE is to be installed, all requirements for new facilities shall apply. All building-level supervisory controllers and field controllers shall be programmed exclusively through Niagara Workbench’s graphical block-based “Wire Sheet” programming environment. The use of any script-based or text-based programming methods, including but not limited to Script Programs, BQL logic, PX scripts, or proprietary vendor scripting tools, is strictly prohibited. All programming logic must be constructed using standard Niagara 4 block logic components only. Each control sequence shall be fully represented and editable in the Wire Sheet view for transparency, ease of maintenance, and consistency with Eglin AFB programming standards.

- All graphics (including floor plans) must be updated in both the JACE and the existing Enterprise Network Server (ENS) located in Building 696, which serves as the web server for the system.

- The system shall allow Civil Engineer (CE) technicians to connect to all controllers with Niagara Workbench from Building 696 via the local area network (LAN) to perform all programming, backups, downloads, configurations, and maintenance functions as if directly connected to the device.

- Provide all field controller software necessary for the project Provide the latest Niagara Workbench software version that matches the ENS and USB adapters for each type of DDC field controller, including factory-installed controllers. (This laptop will be verified and used during training.)

- All hardware and software administrator-level passwords shall be provided to the government for access to all levels of all controllers, including Niagara Framework controllers. Provide complete system topology, hardware/software inventory, and configuration documentation.

- All field controllers shall communicate using the BACnet/IP protocol.

- The BACnet communication bus shall be daisy-chained to the JACE. No additional switches or routers shall be used. Care shall be taken not to damage or cut the existing communication bus line for the remainder of the facility.

Energy Management Control System (EMCS) and/or Direct Digital Control (DDC) System Graphics Requirements

1. Graphics shall be in the existing ENS (Enterprise Network Server) located in building 696 which shall serve as the Web Server for the system, as well as in the JACE controller.

2. Include date and time on all graphic screens.

3. Main Map Graphic- This screen will have a list and link to all the buildings on the entire Eglin AFB complex.

4. Building Graphic- This screen will have a third graphic of the front of the building and a building number.  The following links are required on this page: Back to Main Map, Floor Plans, Alarms, Reports, Schedules, History, and User Service.

5. Floor Plan Graphic The floor plan will be 3D with color coded zones, room numbers, and as- built sensor and equipment locations. The following points are required on this page: room temp, room humidity, occupancy status.

The following links are required on this page: Back to Building Graphic, All Equipment (Click on sensor or equipment shown on the floor plan and the link will go to the corresponding equipment).

6. Typical VAV Table Graphic

The VAV table should include the following info:

VAV-Box #, Zone Temp, Set Points (Heat & Cool), SP Source, Flow SP, Flow, Damper position, Heating %, SAT

7. Typical Equipment Graphic

Include a header with equipment type and number, room numbers and area(s) served.

Include all points on the equipment graphic.

The following points will be animated:   fans, dampers, coils, pumps, boilers.

All set points will have the capability of being changed from the graphic.

The following links are required on this page: Back to Floor Plan, provide a hidden link over each point to show an hourly third day trend, provide a hidden link over each point to override all outputs. Provide a link to a spreadsheet with manufacturer and part numbers and warranty dates for all parts on the equipment graphic.

8. Communication Bus Graphic

Include an as-built wiring diagram of the communication bus between all controllers.

9. Provide a printed copy of the graphics prior to project training.

Eglin AFB

Energy Management Control System (EMCS) Network Requirements for New Facilities

- Comm Squadron shall Install/Identify 2 fiber strands dedicated for DDC connectivity.

- Contractor shall install and program a Cisco 8-port switch compatible with the Jace and DDC (ENS). The 796th CES will provide the IP address, VLAN, username and password to the contractor. Contractor will install a fiber patch cord from the 8-port switch to the fiber ports designated by the Communications Squadron.

- Contractor installs a wall mounted lockable network enclosure (LNE) with surge protector for a Cisco 8 port switch-- (see attached LNE Detail)] in the main Communications room mounted on the fire rated backer board.

- Contractor installs a 20A/125V duplex receptacle within 3’ of the LNE for connection of the surge protector. This receptacle shall be connected to the emergency power panel if the building is, or will be, equipped with an emergency generator.

- Contractor installs a single port LAN connection inside the LNE and inside each building level supervisory controller.

- Contractor installs a 2” EMT conduit from the LNE to each building level supervisory controller in the building.

- Contractor installs a 1 ¼” pliable raceway, w/pull string, from the LNE to a height approximately 12” above the Communications room rack. [DDC shop personnel shall install a fiber jumper from the LNE to the installed fiber patch panel].

- Contractor installs purple Cat 6E cable from the LNE to each building level supervisory controller. Note: If the distance exceeds 100 meters between the LNE and the building level supervisory controller, the building level supervisory controller shall be moved, or fiber w/media converters must be used.