## RFI Submission Form
Pre-Proposal RFIs
Submitted By | Date Submitted | Inquiry | Government Response
CMC Building | 2026-05-08 | Is there a specific version number or publication date for the SOW referenced “ICD705”? | Several documents need to be referenced. Intelligence Community Directive (ICD) 705, “Sensitive Compartmented Information Facilities” VERSION 1.5.1 July 26, 2021 Intelligence Community Standard (ICS) 705-1, “Physical and Technical Security Standards for Sensitive Compartmented Information Facilities” 17 SEPTEMBER 2010 Intelligence Community Standard (ICS) 705-2, “Standards for the Accreditation and Reciprocal Use of Sensitive Compartmented Facilities” 22 December 2016 “UNIFIED FACILITIES CRITERIA” (UFC) UFC 4-010-05 Published 26 May 2023
CMC Building | 2026-05-08 | SOW p5, states existing structure is 15,000SF PEB. Are there as-built drawings available for Bldg. 12? | The facility is not a PEB. Yes, there are as-builts of the facility. Attachments will include as-builts to include the floor plan with other divisions.
CMC Building | 2026-05-08 | Are there any drawings available for the work currently being performed in Bldg. 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
CMC Building | 2026-05-08 | Will there be any areas of the building occupied during the performance of this project. | Yes, once the contractor finishes the current construction the user will move from one side to the other.
CMC Building | 2026-05-08 | Will there be any construction phasing requirements? | No construction phasing is required for this task. | notes
CMC Building | 2026-05-08 | SOW p6, 3.2, second paragraph mentions “RF Shielding”. There are no other references to RF Shielding in the SOW except for mechanical penetrations in 3.2. Please confirm requirement for RF Shielding, and degree of RF Attenuation if required. | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19. | Rm 1014 Waveform lab. will require RF shielding. Level of classification A (TS/SCI, SAP) | Room 1032 will only have access fromo the data lab (RM 1028). Room 1033 will only have access from the secured hallway.
CMC Building | 2026-05-08 | SOW p6, 3.1, states perimeter walls will be STC50. ICD705 Wall Type “A” construction indicates two layers 5/8” GWB ea. side for Sound Group 4/STC 50 or better. Is this acceptable? | Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
CMC Building | 2026-05-08 | Are there any specific construction requirements for interior wall partitions and interior doors? | The waveform lab requires RF Shielding. All solid interior wall/doors/rooms should be sound proof to satisfy ICD 705 requirements. This excludes cubicles and cubicle partitions. Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
CMC Building | 2026-05-08 | SOW p6, 3.1 references “true ceiling”, please clarify what constitutes a “true ceiling” in building 12. Will the existing roof assembly suffice as a “true ceiling”? | Walls must go from floor slab (true floor) to underside of floor or roof deck (true ceiling). Reference UFC 4-010-05 Published 26 May 2023
CMC Building | 2026-05-08 | Will STC-50 labeled doors be acceptable as far as STC requirements go? Note that door labels are lab-tested value, not a field-tested value. Field tests typically lose 2-4 points from the published lab-test value. | Yes STC-50 Labeled Doors the space is required to meet the STC requirements so must meet field tested values
CMC Building | 2026-05-08 | SOW p8, 3.4 references “TEMPEST”. Will this 5000sf SCIF be a TEMPEST certified facility as stated in Design Review requirement in 3.6? | That is correct, the TEMPEST certified space boundary is shown in p5 with an orange boundary line (~5000sf). Level A
CMC Building | 2026-05-08 | Will review meetings require all team members attendance in-person at Eglin AFB, or will there be remote attendance/on-line review meetings? | in- person attendance is prefered.
CMC Building | 2026-05-08 | FPE Main Service SOW 3.4 requires removal/replacement of all FPE panels in the project area, fed from the MDP. Field observation indicates the existing MDP is itself an FPE panel. Please confirm whether replacement of this panel is within this scope. | that is correct, the replacement of the MDP will be part of this project task.f
CMC Building | 2026-05-08 | Generator Fuel Type: Is natural gas available at the proposed generator location, or is diesel required? | Per UFC 3-540-01 - For the Air Force: Natural gas systems are not allowed. Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
CMC Building | 2026-05-08 | Emergency Power Classification & Runtime Per SOW 3.8, confirm NEC classification (Article 700, 701, or 702) for the standby system and provide the required generator runtime / fuel tank sizing basis. Eglin Design Manual A14.3 item 14 establishes a 24-hour minimum for RPIE generators; please confirm whether 24 hours is the required basis or if a longer mission duration applies. | No longer mission duration required. Per Eglin Engineering Design Manual: RPIE generators will have a minimum 24-hour local capacity based on the actual generator load fuel consumption rate of the engine.
CMC Building | 2026-05-08 | Rack Count Discrepancy SOW 3.1 indicates 30 racks; Attachment 5 (Bldg 12 Facilities Planning) indicates 20 racks. Please confirm the total rack count for design. | The area for racks are finite and 20-30 racks was the estimate, so 20 should be considered the threshold and 30 the objective.
CMC Building | 2026-05-08 | Server Room Heat Load SOW 3.1/3.2 specifies N+1 CRAC units but no load density. Please provide kW/rack (or total IT load) and confirm N+1 vs 2N intent for CRAC, PDU, and generator sizing. | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
CMC Building | 2026-05-08 | Adjacent Project Drawings Can the Government provide electrical drawings for the adjacent SABER project currently under construction within Building 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
CMC Building | 2026-05-08 | TEMPEST Level SOW 3.6 requires a formal TEMPEST review. Please identify the assigned TEMPEST level. | Level A
CMC Building | 2026-05-08 | Occupancy During Outage: Is Building 12 intended to remain occupied and under normal operation during utility power outages? | Yes, power outages need to be coordinated with the user within 2 weeks.
CMC Building | 2026-05-08 | Generator Location and Site Civil Scope Please identify the assumed generator location, distance from the building, and confirm whether site civil work (concrete pad, bollards, fence/screening, underground feeder routing, trenching, restoration) is included in the base bid scope. | A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
CMC Building | 2026-05-08 | Drive Isolation Transformers for VFDs Eglin Design Manual requires drive isolation transformers for all VFDs. Confirm whether drive isolation transformers are required on this project. | Confirmed, that is correct IAW the most current version of the Eglin Design Guide
CMC Building | 2026-05-08 | Will the server room be considered “incidental equipment” per ufc 3-600-01 and TSFPEWG-G-3-600-01-01-18? If not, what MAC category is the equipment? This will be needed to determine special fire protection requirements such as early warning smoke detection and clean agent fire suppression. | NIST 800-53 PE-13 server room must be considered mission critical.
CMC Building | 2026-05-08 | The existing fire sprinkler appears to be original to the building. Will the sprinkler system remain and only be modified to suit the new floor plan and ceiling or will the sprinkler system in the area of work need to be replaced completely? | the sprinkler system is to remain and will only be modified to suit the new space.
CMC Building | 2026-05-08 | The existing fire sprinkler riser is located where the new server room will be located. Will the fire sprinkler riser remain in the same location or will it be required to be relocated? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. The fire inspector requested to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
CMC Building | 2026-05-08 | Will the existing fire alarm be replaced with fire alarm/mns in the other portion of the building currently under construction before this project is completed? | The exisiting fire alarm panel will be installed from another project, but all new fire alarms will either be tied into the main facility fire alarm panel, or be replaced on an isolated fire alarm panel.
CMC Building | 2026-05-08 | Please confirm a new fire alarm/mass notification system will be required in the area of work. | Yes, the secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor.
CMC Building | 2026-05-08 | Is the existing Monaco transceiver intended to remain and be reused, or be replaced? | The Monaco transceiver will be replaced by another project, however a new system will need to be installed for the secured area.
CMC Building | 2026-05-08 | Per the plumbing site plan on Sheet C-3 dated 6/18/82, the service lateral serving the fire riser is 4 inches. If the fire sprinkler riser is being relocated, is it the Government’s intent to replace the entire service lateral with a new 6-inch or larger line back to the water main? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (the location is to be determine by the design) and a new 6" underground tap line from the water main to the fire riser is required.
CMC Building | 2026-05-08 | Is fall protection required at the roof hatch and new roof-mounted equipment for this project? Please provide fall protection requirements for this project. | Yes, railings at the roof hatch and a administrative control access zone with a visible line 10 ft from the edge of the roof or railing around entire perimeter of roof
CMC Building | 2026-05-08 | Is cybersecurity required? If so, please provide the detailed cybersecurity requirements for the project. | YES. Cybersecurity is required for the information system inside the space. Collateral systems are managed under RMF using AFI 17-101 and NIST SP-800-53 rev5. SAP systems are managed under RMF using the Joint SAP Implementation Guide (JSIG) 2018 w/errata. Open office area & Data Lab (rms 12- 9) classification (TS/SCI, SAP) (NIST 800-53, CNSSI 1253, JSIG, IC Tech Spec - for ICD/ICS 705 domain-specific policies and procedures.)
CMC Building | 2026-05-08 | Will the contractor be required to cover and protect any existing to-remain equipment, or will the user remove all existing equipment prior to construction? | The user will remove all existing equipment/furniture prior construction
CMC Building | 2026-05-08 | What are the cooling requirements for the interior spaces? | Environmental control baselines required by NIST SP 800-53 PE-14 The contractor shall design and construct the interior IT space cooling systems to the following user requirements: The mechanical cooling system shall be sized to continuously cool a dedicated IT equipment load of 2.0 MW. The Computer Room Air Conditioning (CRAC) and chilled water infrastructure shall be designed and installed with N+1 redundancy. The Chilled Water Plant and all CRAC units must be connected to and supported by the 5.0 MW standby generator upon loss of utility power. Thermal Envelope (PE-14 Acceptable Levels): The facility must continuously maintain the interior IT spaces in accordance with ASHRAE TC 9.9 Class A1 and UFC 3-410-01 parameters: Temperature: 64.4°F to 80.6°F (18°C to 27°C) Dew Point: 41.9°F to 59.0°F (5.5°C to 15°C) Maximum Relative Humidity: 60%
CMC Building | 2026-05-08 | What are the humidity requirements for the interior spaces? | NIST 800-53 PE-14
CMC Building | 2026-05-08 | Please describe type of activity and room type/function of each room that requires HVAC in the scope of this project. This information will be used to optimize the HVAC equipment size and layout. Provide as much detail as possible. | The project consist of 3 major spaces Data server (SCIF) Open workoffice space. (SCIF) NEW restroom space. (Common space)
CMC Building | 2026-05-08 | Can the users provide a list of heat producing equipment or the heat load for the interior spaces? | TOTAL IT load 800KW.
CMC Building | 2026-05-08 | Can the current facility users relocate during construction? Will any temporary facilities or cooling be required for the users? | the user will be moved on the same building outside of project area. No temporary facility or cooling is required for this task.
CMC Building | 2026-05-08 | Will there be existing to remain building DDC to tie into? Or will new work be separate? | NEW DDC system will be required to tie to the existing Eglin AFB BACnet.
CMC Building | 2026-05-08 | What is the state of the existing Energy Management Controls System (EMCS)? Any existing drawings or controls diagrams of the existing EMCS? | As-built drawings will be provided. Please refer to Eglin Design Guide dated March 2025 section A11.1.3.1
OAC Construction | 2026-05-11 | Is there a specific version number or publication date for the SOW referenced “ICD705”? This publication is not included in the “Design References” list on page 21 of 24 in the SOW. | Several documents need to be referenced. Intelligence Community Directive (ICD) 705, “Sensitive Compartmented Information Facilities” VERSION 1.5.1 July 26, 2021 Intelligence Community Standard (ICS) 705-1, “Physical and Technical Security Standards for Sensitive Compartmented Information Facilities” 17 SEPTEMBER 2010 Intelligence Community Standard (ICS) 705-2, “Standards for the Accreditation and Reciprocal Use of Sensitive Compartmented Facilities” 22 December 2016 “UNIFIED FACILITIES CRITERIA” (UFC) UFC 4-010-05 Published 26 May 2023
OAC Construction | 2026-05-11 | SOW p5, states existing structure is 15,000SF PEB. Are there as-built drawings available for PEB Bldg. 12? | The facility is not a PEB. Yes, there are as-builts of the facility. Attachments will include as-builts to include the floor plan with other divisions.
OAC Construction | 2026-05-11 | Are there any drawings available for the work currently being performed in Bldg. 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
OAC Construction | 2026-05-11 | Will there be any areas of the building occupied during the performance of this project? | the user will be relocated in the same building but outside from the project area. No temporary facility or cooling is required for this task.
OAC Construction | 2026-05-11 | Will there be any phasing requirements? | No, construction phasing is required for this task.
OAC Construction | 2026-05-11 | SOW p6, 3.2, second paragraph mentions “RF Shielding”. There are no other references to RF Shielding in the SOW except for mechanical penetrations in 3.2. Please confirm requirement for RF Shielding, and degree of RF Attenuation if required. | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19.
OAC Construction | 2026-05-11 | SOW p6, 3.1, states perimeter walls will be STC50. ICD705 Wall Type “A” construction indicates two layers 5/8” GWB ea. side for Sound Group 4/STC 50 or better. Is this acceptable? | Per IC Tech Spec - for ICD/ICS 705. - Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
OAC Construction | 2026-05-11 | Are there any specific requirements for interior partition and doors construction? | Per IC Tech Spec - for ICD/ICS 705. - Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
OAC Construction | 2026-05-11 | SOW p6, 3.1 references “true ceiling”, please clarify what constitutes a “true ceiling” in building 12. Will the existing roof assembly suffice? | Walls must go from floor slab (true floor) to underside of floor or roof deck (true ceiling). Reference UFC 4-010-05 Published 26 May 2023
OAC Construction | 2026-05-11 | Will STC-50 labeled doors be acceptable as far as STC requirements go? Note that door labels are lab-tested value, not a field-tested value. | Yes STC-50 Labeled Doors
OAC Construction | 2026-05-11 | SOW p8, 3.4 references “TEMPEST”. Will this 5000sf SCIF be a TEMPEST certified facility as stated in Design Review requirement in 3.6? | That is correct, the TEMPEST certified space boundary is shown in p5 with an orange boundary line (~5000sf). Level A
OAC Construction | 2026-05-11 | Will review meetings require attendance in-person at Eglin AFB, or on-line? | in- person attendance is prefered.
OAC Construction | 2026-05-11 | In the RFP Attachment 5, Diagram 2, there is a long thin space to the plan west of Room 7. What is the purpose of this space? | In accordance with the TEMPEST Room Diagram Template, this space is configured to house a GSA-approved secure safe and multi-function printers.
OAC Construction | 2026-05-11 | In the RFP Attachment 5, Diagram 2, there is a red line defining the complete perimeter. Is this the ICD705 secure perimeter? Are there no secure compartments within this secure perimeter? | Correct, the Red perimeter line defines the SCIF boundary.
OAC Construction | 2026-05-11 | The RFP SOW, p2 Existing Building Conditions states there is an ACM Survey dated 12/13/24, can this be provided? | Per the ACM Survey dated 12/13/24. hazmat has been found and abated on certain areas of the building. This survey does not show any samples within the specific project footprint. Therefore, the contractor must include the cost of localized pre-demolition testing in their proposal. To ensure a fair bidding environment for the abatement (removal) portion, all bidders shall include a fixed allowance of $25,000 in their proposal for potential ACM abatement. If ACM is discovered during testing, it will be paid out of this allowance based on actual verified costs. If no ACM is found, the unused allowance funds will be returned to the Government.
OAC Construction | 2026-05-11 | The RFP SOW requires 18” raised access floor in the server room, is there a waiver for handicap-access? Or an 18’ ramp will be required. | the ramp is required. However, the minimum height for the raised floor will be determined by the design, considering space for cabling and hvac .
OAC Construction | 2026-05-11 | Is there a basis of design to use for Bid Option 001 FF&E? | there is a layout plan and user space intention but a full interior design plan is required as part of this task.
OAC Construction | 2026-05-11 | Is fall protection required for this project? Please provide fall protection requirements for this project. | yes, railings at the roof hatch and a administrative control access zone with a visible line 10 ft from the edge of the roof or railing around entire perimeter of roof
OAC Construction | 2026-05-11 | Is cybersecurity required? If so, please provide the detailed cybersecurity requirements for the project. | YES. Cybersecurity is required for the information system inside the space. Collateral systems are managed under RMF using AFI 17-101 and NIST SP-800-53 rev5. SAP systems are managed under RMF using the Joint SAP Implementation Guide (JSIG) 2018 w/errata. Open office area & Data Lab (rms 12- 9) classification (TS/SCI, SAP) (NIST 800-53, CNSSI 1253, JSIG, IC Tech Spec - for ICD/ICS 705 domain-specific policies and procedures.)
OAC Construction | 2026-05-11 | Will the contractor be required to cover and protect any existing to remain equipment, or will the user remove all existing equipment prior to construction? | the user will remove of all equipment/furniture currently in the construction space.
OAC Construction | 2026-05-11 | What are the cooling requirements for the spaces? | Environmental control baselines required by NIST SP 800-53 PE-14 The contractor shall design and construct the interior IT space cooling systems to the following user requirements: The mechanical cooling system shall be sized to continuously cool a dedicated IT equipment load of 800 KW. The Computer Room Air Conditioning (CRAC) and chilled water infrastructure shall be designed and installed with N+1 redundancy. The Chilled Water Plant and all CRAC units must be connected to and supported by the standby generator upon loss of utility power. Thermal Envelope (PE-14 Acceptable Levels): The facility must continuously maintain the interior IT spaces in accordance with ASHRAE TC 9.9 Class A1 and UFC 3-410-01 parameters: Temperature: 64.4°F to 80.6°F (18°C to 27°C) Dew Point: 41.9°F to 59.0°F (5.5°C to 15°C) Maximum Relative Humidity: 60%
OAC Construction | 2026-05-11 | What are the humidity requirements for the spaces? | NIST 800-53 PE-14
OAC Construction | 2026-05-11 | Please describe type of activity and room type/function of each room that requires HVAC in the scope of this project. This information will be used to optimize the HVAC equipment size and layout. Provide as much or as little detail as allowed. | The project consist of 3 major spaces Data server (SCIF) Open workoffice space. (SCIF) NEW restroom space. (Common space)
OAC Construction | 2026-05-11 | Can the users provide a list of heat producing equipment or the heat load for the spaces? | TOTAL IT 800KW
OAC Construction | 2026-05-11 | Can the users relocate during construction? Will any temporary facilities or cooling be required for the users? | the users will be relocated in the same building but outside from the project area. No temporary facility or cooling is required for this task.
OAC Construction | 2026-05-11 | Will there be existing to remain building DDC to tie into? Or will new work be separate? | NEW DDC system will be required to tie to the existing Eglin AFB BACnet.
OAC Construction | 2026-05-11 | What is the state of the existing Energy Management Controls System (EMCS)? Any existing drawings or controls diagrams of the existing EMCS? | As-built drawings will be provided. Please refer to Eglin Design Guide dated March 2025 section A11.1.3.1
OAC Construction | 2026-05-11 | FPE Main Service. SOW 3.4 requires removal/replacement of all FPE panels in the project area, fed from the MDP. Field observation indicates the existing MDP is itself an FPE panel. Please confirm whether replacement of this panel is within this scope. | That is correct, Existing (FPE) MDP will be replaced
OAC Construction | 2026-05-11 | Generator Fuel Type. Is natural gas available at the proposed generator location, or is diesel required? | Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
OAC Construction | 2026-05-11 | Emergency Power Classification & Runtime. Per SOW 3.8, confirm NEC classification (Article 700, 701, or 702) for the standby system and provide the required generator runtime / fuel tank sizing basis. Eglin Design Manual A14.3 item 14 establishes a 24-hour minimum for RPIE generators; please confirm whether 24 hours is the required basis or if a longer mission duration applies. | No longer mission duration required. Per Eglin Engineering Design Manual: RPIE generators will have a minimum 24-hour local capacity based on the actual generator load fuel consumption rate of the engine.
OAC Construction | 2026-05-11 | Rack Count Discrepancy. SOW 3.1 indicates 30 racks; Attachment 5 (Bldg 12 Facilities Planning) indicates 20 racks. Please confirm the total rack count for design. | 30 racks
OAC Construction | 2026-05-11 | Server Room Heat Load. SOW 3.1/3.2 specifies N+1 CRAC units but no load density. Please provide kW/rack (or total IT load) and confirm N+1 vs 2N intent for CRAC, PDU, and generator sizing. | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
OAC Construction | 2026-05-11 | Adjacent Project Drawings. Can the Government provide electrical drawings for the adjacent project currently under construction within Building 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
OAC Construction | 2026-05-11 | TEMPEST Level. SOW 3.6 requires a formal TEMPEST review. Please identify the assigned TEMPEST level. | Level A
OAC Construction | 2026-05-11 | Occupancy During Outage. Is Building 12 intended to remain occupied and under normal operation during utility power outages? | Yes, power outages need to be coordinated with the user within 2 weeks.
OAC Construction | 2026-05-11 | Generator Location and Site Civil Scope. Please identify the assumed generator location, distance from the building, and confirm whether site civil work (concrete pad, bollards, fence/screening, underground feeder routing, trenching, restoration) is included in the base bid scope. | Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
OAC Construction | 2026-05-11 | Drive Isolation Transformers for VFDs and/or EC motors. Eglin Design Manual requires drive isolation transformers for all VFDs. Confirm whether drive isolation transformers are required on this project. | Confirmed, that is correct IAW the most current version of the Eglin Design Guide
OAC Construction | 2026-05-11 | Will the server room be considered “incidental equipment” per ufc 3-600-01 and TSFPEWG-G-3-600-01-01-18? If not, what MAC category is the equipment? This will be needed to determine special fire protection requirements such as early warning smoke detection and clean agent fire suppression. | NIST 800-53 PE-13 server room must be considered mission critical.
OAC Construction | 2026-05-11 | The existing fire sprinkler appears to be original to the building. Will the sprinkler system remain and only be modified to suite new floor plan and ceiling or will the sprinkler system in the area of work need to be replaced completely? | the intent is to modify the system to suit the new space. The request from the fire inspector is to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility.
OAC Construction | 2026-05-11 | The existing fire sprinkler riser is located where the new server room will be located. Will the fire sprinkler riser remain in the same location or will it be required to be relocated? | the contractor is responsible to determine a new location for the fire riser and a tie connection point. The fire inspector has indicated that all sprinkler heads need to be changed out of the entire facility. A test will be conducted of the sprinkler system on another project.
OAC Construction | 2026-05-11 | Will the existing fire alarm be replaced with fire alarm/mns in the other portion of the building before this project is completed? | The exisiting fire alarm panel will be installed from another project, but all new fire alarms will either be tied into the main facility fire alarm panel, or be replaced on an isolated fire alarm panel.
OAC Construction | 2026-05-11 | Please confirm a new fire alarm/mass notification system will be required in the area of work. | Yes, the secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor.
OAC Construction | 2026-05-11 | Is the existing Monaco transceiver intended to remain and be reused, or be replaced? | The Monaco transceiver will be replaced by another project, however a new system will need to be installed for the secured area.
OAC Construction | 2026-05-11 | Per the plumbing site plan on Sheet C-3 dated 6/18/82, the service lateral serving the fire riser is 4 inches. If the fire sprinkler riser is being relocated, is it the Government’s intent to replace the entire service lateral with a new 6-inch or larger line back to the water main? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. The fire inspector requested to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
OAC Construction | 2026-05-11 | Have finish selections been addressed that can be used as a basis of design? If so, will that information be available to the design team after award. | finishes selection is to be determined with the user during Design phase.
OAC Construction | 2026-05-11 | Are there any special furniture features or finish requirements? | Design, general construction, and finishing work must be performed by U.S. companies using U.S. citizens
OAC Construction | 2026-05-11 | Please identify all Government Furnished Equipment (GFE) associated with this project including UPS systems, IDS equipment, ACS equipment, telecom electronics, server racks, monitoring equipment, and network switches. | per SOW section 3.5 - Security "contarctor responsible to provide infrastructure pathways for the IDS and ACS systems." no wiring or equipment is required.
OAC Construction | 2026-05-11 | Please provide specifications and approved manufacturers for the GSA Class 5 vault door and identify all acoustic, forced-entry, and emergency egress requirements associated with the SCIF entrances. | General Services Administration (GSA)-approved Class 5 vault door equipped to meet Architectural Barriers Act (ABA) Standards. General Services Administration (GSA) has authorized the use of federal specification AA-D-600D for vault doors. Reference UFC 4-010-05 Published 26 May 2023 to answer this question in its entirety to include emergency egress requirements.
OAC Construction | 2026-05-11 | Please clarify whether the required Arc Flash Hazard Analysis applies only to newly installed equipment or to the entire affected electrical distribution system. | In accordance with UFC 3-501-01, because we are replacing the main distribution panel (MDP) and all downstream Federal pacific (FPE panels within the project boundary, the required Arc Flash Hazard Analysis must apply to the affected electrical distribution system.
OAC Construction | 2026-05-11 | Please identify the existing telecommunications demarcation location and all existing available pathways intended for classified and unclassified network distribution. | as-built drawings will provided. Per SOW 3.6 DESIGN ELEMENT SIX – TELECOMMUNICATIONS. The contractor shall provide physically separate and isolated pathway systems for Classified (Red) and Unclassified (Black) networks. The Red pathway system shall be constructed using 100% Rigid Metallic Conduit (RMC) from the point of entry into the SCIF to the final termination point. Design must include the installation of new optic fiber cabling, separate color-coded patch panels, and separate equipment racks for both networks within the Secure Server Room.
OAC Construction | 2026-05-11 | Please clarify the required fiber optic cabling scope including strand counts, fiber type, testing requirements, and termination requirements. | Outside plant: The 96 CS is providing 48 strand single Mode fiber and doing the testing for it, running to the orig "soda room" Inside Plant: TBD
OAC Construction | 2026-05-11 | Please clarify whether existing underground sanitary and domestic water utilities have been camera inspected or otherwise evaluated for suitability for reuse. | Based on the conditions of the existing sanitary sewr system, it Is required to replaced the entire kitchen sewer system to include grease traps and piping, potentially cap and abandone in place, and install new sewer system piping to suit the new restroom space needs all the way to the gravity main service line.
OAC Construction | 2026-05-11 | Please clarify the extent of ADA upgrades required beyond the restroom renovation area including sidewalks, entrances, parking, ramps, hardware, and path-of-travel improvements. | the building already have ADA access to the space.
OAC Construction | 2026-05-11 | Please clarify whether procurement of long-lead materials other than the generator system may proceed prior to completion of final design approval. | open to discussion
OAC Construction | 2026-05-11 | Please clarify whether contract time extensions will be granted for Government review | Time extensions will be granted for Government delays. The Period of Performance at time of award is for design and build and is expected that all elements of Design-Build will be acomplished during the period of Performance.
Onopa Services | 2026-05-11 | Is there a specific version number or publication date for the SOW referenced “ICD705”? | Several documents need to be referenced. Intelligence Community Directive (ICD) 705, “Sensitive Compartmented Information Facilities” VERSION 1.5.1 July 26, 2021 Intelligence Community Standard (ICS) 705-1, “Physical and Technical Security Standards for Sensitive Compartmented Information Facilities” 17 SEPTEMBER 2010 Intelligence Community Standard (ICS) 705-2, “Standards for the Accreditation and Reciprocal Use of Sensitive Compartmented Facilities” 22 December 2016 “UNIFIED FACILITIES CRITERIA” (UFC) UFC 4-010-05 Published 26 May 2023
Onopa Services | 2026-05-11 | SOW p5, states existing structure is 15,000SF PEB. Are there as-built drawings available for Bldg. 12? | The facility is not a PEB. Yes, there are as-builts of the facility. Attachments will include as-builts to include the floor plan with other divisions.
Onopa Services | 2026-05-11 | Are there any drawings available for the work currently being performed in Bldg. 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Onopa Services | 2026-05-11 | Will there be any areas of the building occupied during the performance of this project. | The users will be relocated in the same building but outside from the project area. No temporary facility or cooling is required for this task.
Onopa Services | 2026-05-11 | Will there be any construction phasing requirements? | No construction phasing is required for this task.
Onopa Services | 2026-05-11 | SOW p6, 3.2, second paragraph mentions “RF Shielding”. There are no other references to RF Shielding in the SOW except for mechanical penetrations in 3.2. Please confirm requirement for RF Shielding, and degree of RF Attenuation if required. | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19.
Onopa Services | 2026-05-11 | SOW p6, 3.1, states perimeter walls will be STC50. ICD705 Wall Type “A” construction indicates two layers 5/8” GWB ea. side for Sound Group 4/STC 50 or better. Is this acceptable? | Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides.
Onopa Services | 2026-05-11 | Are there any specific construction requirements for interior wall partitions and interior doors? | Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
Onopa Services | 2026-05-11 | SOW p6, 3.1 references “true ceiling”, please clarify what constitutes a “true ceiling” in building 12. Will the existing roof assembly suffice as a “true ceiling”? | Walls must go from floor slab (true floor) to underside of floor or roof deck (true ceiling). Reference UFC 4-010-05 Published 26 May 2023
Onopa Services | 2026-05-11 | Will STC-50 labeled doors be acceptable as far as STC requirements go? Note that door labels are lab-tested value, not a field-tested value. Field tests typically lose 2-4 points from the published lab-test value. | Yes STC-50 Labeled Doors
Onopa Services | 2026-05-11 | SOW p8, 3.4 references “TEMPEST”. Will this 5000sf SCIF be a TEMPEST certified facility as stated in Design Review requirement in 3.6? | That is correct, the TEMPEST certified space boundary is shown in p5 with an orange boundary line (~5000sf). Level A
Onopa Services | 2026-05-11 | Will review meetings require all team members attendance in-person at Eglin AFB, or will there be remote attendance/on-line review meetings? | in- person attendance is prefered.
Onopa Services | 2026-05-11 | FPE Main Service SOW 3.4 requires removal/replacement of all FPE panels in the project area, fed from the MDP. Field observation indicates the existing MDP is itself an FPE panel. Please confirm whether replacement of this panel is within this scope. | that is correct, the replacement of the MDP will be part of this project task.
Onopa Services | 2026-05-11 | Generator Fuel Type: Is natural gas available at the proposed generator location, or is diesel required? | Per UFC 3-540-01 - For the Air Force: Natural gas systems are not allowed. Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
Onopa Services | 2026-05-11 | Emergency Power Classification & Runtime Per SOW 3.8, confirm NEC classification (Article 700, 701, or 702) for the standby system and provide the required generator runtime / fuel tank sizing basis. Eglin Design Manual A14.3 item 14 establishes a 24-hour minimum for RPIE generators; please confirm whether 24 hours is the required basis or if a longer mission duration applies. | No longer mission duration required. Per Eglin Engineering Design Manual: RPIE generators will have a minimum 24-hour local capacity based on the actual generator load fuel consumption rate of the engine.
Onopa Services | 2026-05-11 | Rack Count Discrepancy SOW 3.1 indicates 30 racks; Attachment 5 (Bldg 12 Facilities Planning) indicates 20 racks. Please confirm the total rack count for design. | 30 racks
Onopa Services | 2026-05-11 | Server Room Heat Load SOW 3.1/3.2 specifies N+1 CRAC units but no load density. Please provide kW/rack (or total IT load) and confirm N+1 vs 2N intent for CRAC, PDU, and generator sizing. | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
Onopa Services | 2026-05-11 | Adjacent Project Drawings Can the Government provide electrical drawings for the adjacent SABER project currently under construction within Building 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Onopa Services | 2026-05-11 | TEMPEST Level SOW 3.6 requires a formal TEMPEST review. Please identify the assigned TEMPEST level. | Level A
Onopa Services | 2026-05-11 | Occupancy During Outage: Is Building 12 intended to remain occupied and under normal operation during utility power outages? | Yes, the facility will be occupied during construction.
Onopa Services | 2026-05-11 | Generator Location and Site Civil Scope Please identify the assumed generator location, distance from the building, and confirm whether site civil work (concrete pad, bollards, fence/screening, underground feeder routing, trenching, restoration) is included in the base bid scope. | Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
Onopa Services | 2026-05-11 | Drive Isolation Transformers for VFDs Eglin Design Manual requires drive isolation transformers for all VFDs. Confirm whether drive isolation transformers are required on this project. | Confirmed, that is correct IAW the most current version of the Eglin Design Guide
Onopa Services | 2026-05-11 | Will the server room be considered “incidental equipment” per ufc 3-600-01 and TSFPEWG-G-3-600-01-01-18? If not, what MAC category is the equipment? This will be needed to determine special fire protection requirements such as early warning smoke detection and clean agent fire suppression. | NIST 800-53 PE-13 server room must be considered mission critical.
Onopa Services | 2026-05-11 | The existing fire sprinkler appears to be original to the building. Will the sprinkler system remain and only be modified to suit the new floor plan and ceiling or will the sprinkler system in the area of work need to be replaced completely? | the sprinkler system is to remain and will only be modified to suit the new space.
Onopa Services | 2026-05-11 | The existing fire sprinkler riser is located where the new server room will be located. Will the fire sprinkler riser remain in the same location or will it be required to be relocated? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. The fire inspector requested to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
Onopa Services | 2026-05-11 | Will the existing fire alarm be replaced with fire alarm/mns in the other portion of the building currently under construction before this project is completed? | The exisiting fire alarm panel will be installed from another project, but all new fire alarms will either be tied into the main facility fire alarm panel, or be replaced on an isolated fire alarm panel.
Onopa Services | 2026-05-11 | Please confirm a new fire alarm/mass notification system will be required in the area of work. | Yes, the secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor.
Onopa Services | 2026-05-11 | Is the existing Monaco transceiver intended to remain and be reused, or be replaced? | The Monaco transceiver will be replaced by another project, however a new system will need to be installed for the secured area.
Onopa Services | 2026-05-11 | Per the plumbing site plan on Sheet C-3 dated 6/18/82, the service lateral serving the fire riser is 4 inches. If the fire sprinkler riser is being relocated, is it the Government’s intent to replace the entire service lateral with a new 6-inch or larger line back to the water main? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. The fire inspector requested to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
Onopa Services | 2026-05-11 | Is fall protection required at the roof hatch and new roof-mounted equipment for this project? Please provide fall protection requirements for this project. | yes, railings at the roof hatch and a administrative control access zone with a visible line 10 ft from the edge of the roof or railing around entire perimeter of roof
Onopa Services | 2026-05-11 | Is cybersecurity required? If so, please provide the detailed cybersecurity requirements for the project. | YES. Cybersecurity is required for the information system inside the space. Collateral systems are managed under RMF using AFI 17-101 and NIST SP-800-53 rev5. SAP systems are managed under RMF using the Joint SAP Implementation Guide (JSIG) 2018 w/errata. Open office area & Data Lab (rms 12- 9) classification (TS/SCI, SAP) (NIST 800-53, CNSSI 1253, JSIG, IC Tech Spec - for ICD/ICS 705 domain-specific policies and procedures.)
Onopa Services | 2026-05-11 | Will the contractor be required to cover and protect any existing to-remain equipment, or will the user remove all existing equipment prior to construction? | The user is to move all equipment and vacate space prior construction start. There should be no equipment in the construction space.
Onopa Services | 2026-05-11 | What are the cooling requirements for the interior spaces? | Environmental control baselines required by NIST SP 800-53 PE-14 The contractor shall design and construct the interior IT space cooling systems to the following user requirements: The mechanical cooling system shall be sized to continuously cool a dedicated IT equipment load of 2.0 MW. The Computer Room Air Conditioning (CRAC) and chilled water infrastructure shall be designed and installed with N+1 redundancy. The Chilled Water Plant and all CRAC units must be connected to and supported by the 5.0 MW standby generator upon loss of utility power. Thermal Envelope (PE-14 Acceptable Levels): The facility must continuously maintain the interior IT spaces in accordance with ASHRAE TC 9.9 Class A1 and UFC 3-410-01 parameters: Temperature: 64.4°F to 80.6°F (18°C to 27°C) Dew Point: 41.9°F to 59.0°F (5.5°C to 15°C) Maximum Relative Humidity: 60%
Onopa Services | 2026-05-11 | What are the humidity requirements for the interior spaces? | NIST 800-53 PE-14
Onopa Services | 2026-05-11 | Please describe type of activity and room type/function of each room that requires HVAC in the scope of this project. This information will be used to optimize the HVAC equipment size and layout. Provide as much detail as possible. | The project consist of 3 major spaces Data server (SCIF) Open workoffice space. (SCIF) NEW restroom space. (Common space)
Onopa Services | 2026-05-11 | Can the users provide a list of heat producing equipment or the heat load for the interior spaces? | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
Onopa Services | 2026-05-11 | Can the current facility users relocate during construction? Will any temporary facilities or cooling be required for the users? | the user will be relocated, no temporary facility or or cooling is required for this task.
Onopa Services | 2026-05-11 | Will there be existing to remain building DDC to tie into? Or will new work be separate? | NEW DDC system will be required to tie to the existing Eglin AFB BACnet.
Onopa Services | 2026-05-11 | What is the state of the existing Energy Management Controls System (EMCS)? Any existing drawings or controls diagrams of the existing EMCS? | As-built drawings will be provided. Please refer to Eglin Design Guide dated March 2025 section A11.1.3.1
Onopa Services | 2026-05-11 | There are no front-end specs for QC, Safety, Submittals, Schedule etc. Please clarify | The Quality control (QC), safety, and project schedule must be addresed in the proposal and executed in accordance with base regulations (Eglin Design Guide) UFC, UFGS, and FAR clauses to include FAR clause #52.246-12.
Onopa Services | 2026-05-11 | Can this project be supervised by a Triple-Hat? | NO
Onopa Services | 2026-05-11 | Clarify which existing mechanical, electrical, and plumbing systems are to remain, be removed, or be reused. | Please refer to SOW sections: 3.2 DESIGN ELEMENT TWO – MECHANICAL (HVAC) 3.3 DESIGN ELEMENT THREE – PLUMBING 3.4 DESIGN ELEMENT FOUR – ELECTRICAL
Onopa Services | 2026-05-11 | Provide design criteria and equipment requirements for IDS and access control systems. | per SOW section 3.5 - Security "contarctor responsible to provide infrastructure pathways for the IDS and ACS systems." no wiring or equipment is required.
Onopa Services | 2026-05-11 | Provide IT equipment load criteria including kW per rack, total heat load, redundancy, and future expansion capacity. | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
Onopa Services | 2026-05-11 | Have finish selections been addressed that can be used as a basis of design? If so, will that information be available to the design team after award. | finish selection is to be dtermined by the design
Onopa Services | 2026-05-11 | Are there any special furniture features or finish requirements? | Design, general construction, and finishing work must be performed by U.S. companies using U.S. citizens. Reference TECH SPEC ICS-705-1
Onopa Services | 2026-05-11 | Please provide the attendee sign-in sheet required on the site visit for this project. | is rovided as an attachment
Onopa Services | 2026-05-11 | Please confirm whether this project is Design-Build (DB) or Design-Bid-Build (DBB). | project is Design build
Onopa Services | 2026-05-11 | If this project is Design-Build, please clarify whether the additional submittal requirements identified in the Scope of Work (35%, 65%, 95%, 100% UR, and 100% CF) are required in addition to the 35% and Final submittals identified in the RFP letter. | To maximize the efficiency of this Design-Build project while adhering to strict ICD 705 SCIF accreditation requirements, the government is tailoring the submittal schedule. The contractor shall provide 35%, 95%, and Final (100% CF) design submittals. The 95% submittal is strictly required to verify critical SCIF acoustic and physical security details prior to the issuance of the Final construction documents.
Onopa Services | 2026-05-11 | The Scope of Work references TEMPEST requirements and ICD/ICS 703 requirements. Please confirm whether HEMP shielding is required for this facility. | HEMP Shielding will not be required under this task.
Onopa Services | 2026-05-11 | Please clarify whether demolition of the existing kitchen spaces includes demolition/removal of the existing separation walls. | Yes, Demolition in the kitchen space includes partition walls, kitchen counters and associated casework, coolers, refrigeration units, and associated utility hookups all other specified kitchen fixtures, finishes, and equipment within the designated footprint.
Reasor | 2026-05-11 | Can one individual serve as the Super, QCM and SSHO? | NO
Reasor | 2026-05-11 | Please provide Building 12 "as-built" drawings. | will be provided
Reasor | 2026-05-11 | Section 1.1 Project Description - Existing Conditions states that "As part of the soliciation packages, the Governmenbt is providing an ACM survey report dated 12/13/2024". It doesn’t appear that the ACM report was provide with solicitaiton. Please provide. | Per the ACM Survey dated 12/13/24. hazmat has been found and abated on certain areas of the building. This survey does not show any samples within the specific project footprint. Therefore, the contractor must include the cost of localized pre-demolition testing in their proposal. To ensure a fair bidding environment for the abatement (removal) portion, all bidders shall include a fixed allowance of $25,000 in their proposal for potential ACM abatement. If ACM is discovered during testing, it will be paid out of this allowance based on actual verified costs. If no ACM is found, the unused allowance funds will be returned to the Government.
Reasor | 2026-05-11 | Based on the age of the building and on the statement in the SOW that there is ACM outside of the construction area, it is likely that there will be ACM encountered with the construction limits for this project. Since the contractor is unable to quantify the amount of abatement that may be needed, we respectfuly request that the government provide an estimated quantity for bidding purposase so that all contractors are bidding the same thing. | Per the ACM Survey dated 12/13/24. hazmat has been found and abated on certain areas of the building. This survey does not show any samples within the specific project footprint. Therefore, the contractor must include the cost of localized pre-demolition testing in their proposal. To ensure a fair bidding environment for the abatement (removal) portion, all bidders shall include a fixed allowance of $25,000 in their proposal for potential ACM abatement. If ACM is discovered during testing, it will be paid out of this allowance based on actual verified costs. If no ACM is found, the unused allowance funds will be returned to the Government.
Reasor | 2026-05-11 | Please provide Building 12 exterior Underground Utility "as-built" drawings. | will be provided
Reasor | 2026-05-11 | Section 3.1 Design Element One states that Bldg 12 shall be "redesigned in accordance with a forthcoming Preliminary Concept Floor Plan. Please provide Preliminary Concept Floor Plan. | the user TEMPEST room space Diagram will be proivded.
Reasor | 2026-05-11 | Section 3.1 clearly states perimter walls shall be STC50 rated but does not state need for RF shielding. Section 3.2 HVAC 2nd paragraph references compliance with ICD 705 "RF shielding". Please clarify if RF shielding will be required for this project. | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19.
Reasor | 2026-05-11 | Are there any available drawings from the current renovation project being completed by Kekolu Contracting? If so can they be provided to aid in development of price proposal? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Reasor | 2026-05-11 | Will the new restroom area service both the secure space and the area currently be renovated? | that is correct the new restroom will served both areas
Reasor | 2026-05-11 | Please provide the current contracted SOW and drawings for the existing renovation project so the contractor can see extent of renovation. For example is the hallway and rooms outside of the proposed new restroom limits being renovated under existing contract? If it is not getting renovated how do we transition from newly renovated space to partially demolished space? | the extent of the project is shown in figure 3. The 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Reasor | 2026-05-11 | Will the area of construction be occupied during construction? | portions of the building will be occupied by the user. Project area will be vacated during construction.
Reasor | 2026-05-11 | Will the current occupants within the limits of construction be moved to area being renovated now? | This is correct, portions of the building will be occupied by the user, however the boundaries within this project will be vacated during construction.
Reasor | 2026-05-11 | There appears to be abandoned roof top equipment. What items on roof are currently not functional and is the contractor to demo/remove non used equipment? | that is correct, the unit above the project space is currently serving Rooms 1027, 1028, 1029, 1030,1031 and the restrooms on the other dside of the building (1024, 1025). The intent is to remove existing system serving this area and install a new HVAC system that suit the mission of the new SCIF space and new restroom. the non used equipment above this space will be demo/removed.
Reasor | 2026-05-11 | The scope calls for a new dedicate roof top unit for the ICD workspace and a new roof top exhaust fan for the restroom and two CRAC units for the Server rooms. Is the exisitng RTU over the proposed ICD space, defective? It appears to relatively recent? | new dedicated RTU system to serve the new SCIF work office space, a new exhaust fan system and dedicated aoutdoor air unit to serve the new restroom area, two (2) new Computer Room Air Conditioning (CRAC) units, installed in an N+1 redundant configuration. The system shall be sized to handle the full design heat load with one unit operating. designed to discharge conditioned air into the raised access floor plenum. all heating systems, including RTU, DOAs, CRAC reheat functions, shall be electric.
Reasor | 2026-05-11 | The SOW calls for new RTU over ICD workspace. There is an exisitng RTU over this space. The SOW is not clear if this RTU is to be demolished as part of this scope. Please clarify. | existing unit is to be removed and a new system will be put in place. To meet mission needs.
Reasor | 2026-05-11 | How is the contractor to bid the FF&E option with out a conceptual floor plan or furniture requirements or quantity of furniture? Please provide FF&E requirements | the user TEMPEST room space Diagram will be proivded. However, The contractor shall provide all professional services and coordination required to develop a comprehensive, non-proprietary FF&E Procurement Data Package. This effort shall include all programming to define functional and operational requirements, space planning to create detailed furniture layouts, and the selection and specification of all furniture, fixtures, equipment, materials, and finishes.
Reasor | 2026-05-11 | Design Element 1 3rd paragraph it states that a GSA Class 5 vault door will be needed for main entrance. Please identify where the main entrance is to be located. | The main entrance to the SCIF thru the building interior, by the open office workspace to the EAST.
Reasor | 2026-05-11 | Design Element 3 Plumbing states to utilize sanitary and domestic water lines where feasible. Please provide under slab piping as builts and plumbing as builts to determine locations of plumbing. | Based on the current conditions of the existing sanitary sewr system, it Is required to replaced the entire kitchen sewer system to include grease traps and piping potentially cap and abandone in place, and install new sewer system piping to suit the new restroom needs.
Reasor | 2026-05-11 | During the site visit it was observed that there is a fire suppression and fire alarm system within the construction limits. However, fire suppression and fire alarm are not addressed in the scope of work. Please clarify if fire suppression and fire alarm are part of the scope and to what extent. | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. The fire inspector requested to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
Reasor | 2026-05-11 | Please confirm contractor is not required to provide the Accrediting Officer (AO), Construction Security Officer, or Construction Security Plan associated with obtaining the SCIF rating. | No - The AO, and Site Security Manager are government personnel and the CSP is the plan created by the Site Security Manager and presented to the AO for approval.
Reasor | 2026-05-11 | Will this project require US citizens? | Per the Intelligence Community Technical Specifications for SCIF Construction (IC Tech Spec v1.5.1, Chapter 13) General construction of SCIFs shall be performed using U.S. citizens and U.S. Firms.
Reasor | 2026-05-11 | Will this project require natural born US citizens? | No, the requirement that US Companies and US Citizens do the construction does not require the persons to be Natural born US Citizens.
Reasor | 2026-05-11 | Is independent 3rd party acoustical sound testing required to show STC50 rating for this project? | Yes STC-50 is the minimum threshold for accreditation to be used as a ICD-705 facility
Reasor | 2026-05-11 | If RF shielding is required, will a indepentant 3rd party be requirect for testing? | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19. Yes 3rd party testing is required
Reasor | 2026-05-11 | Will Div 25 Cybersecurity be required for this project? | YES. Cybersecurity is required for the information system inside the space. Collateral systems are managed under RMF using AFI 17-101 and NIST SP-800-53 rev5. SAP systems are managed under RMF using the Joint SAP Implementation Guide (JSIG) 2018 w/errata. Open office area & Data Lab (rms 12- 9) classification (TS/SCI, SAP) (NIST 800-53, CNSSI 1253, JSIG, IC Tech Spec - for ICD/ICS 705 domain-specific policies and procedures.)
Reasor | 2026-05-11 | Is there a specific version number or publication date for the SOW referenced “ICD705”? This publication is not included in the “Design References” list on page 21 of 24 in the SOW. | Several documents need to be referenced. Intelligence Community Directive (ICD) 705, “Sensitive Compartmented Information Facilities” VERSION 1.5.1 July 26, 2021 Intelligence Community Standard (ICS) 705-1, “Physical and Technical Security Standards for Sensitive Compartmented Information Facilities” 17 SEPTEMBER 2010 Intelligence Community Standard (ICS) 705-2, “Standards for the Accreditation and Reciprocal Use of Sensitive Compartmented Facilities” 22 December 2016 “UNIFIED FACILITIES CRITERIA” (UFC) UFC 4-010-05 Published 26 May 2023
Reasor | 2026-05-11 | SOW p5, states existing structure is 15,000SF PEB. Are there as-built drawings available for PEB Bldg. 12? | The facility is not a PEB. Yes, there are as-builts of the facility. Attachments will include as-builts to include the floor plan with other divisions.
Reasor | 2026-05-11 | Are there any drawings available for the work currently being performed in Bldg. 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Reasor | 2026-05-11 | Will there be any areas of the building occupied during the performance of this project. | Yes, the facility will be occupied during construction.
Reasor | 2026-05-11 | Will there be any phasing requirements? | Phasing plan for construction will not be required for this task.
Reasor | 2026-05-11 | SOW p6, 3.2, second paragraph mentions “RF Shielding”. There are no other references to RF Shielding in the SOW except for mechanical penetrations in 3.2. Please confirm requirement for RF Shielding, and degree of RF Attenuation if required. | Yes, 80-90 dB of attenuation for the waveform laboratory only Level of classification A (TS/SCI, SAP, etc.) and which organization owns the domain (AFSCI, DIA, NSA, etc). NIST 800-53 AC-18(5), PE-19.
Reasor | 2026-05-11 | Are there any specific requirements for interior partition and doors construction? | Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides. Utilize STC 50 rated doors.
Reasor | 2026-05-11 | SOW p6, 3.1, states perimeter walls will be STC50. ICD705 Wall Type “A” construction indicates two layers 5/8” GWB ea. side for Sound Group 4/STC 50 or better. Is this acceptable? | Wall type “A” will be utilized include studs (metal or wood) insulation, gypsum boards (either two on either side or one on the exterior and three on the interior) and 3.5” sounds attenuation material fastened to prevent sliding. Wall framing at STC-rated doors, extend triple-stud jambs Continuous from floor-to-floor structure above, brace each side of door at each side of wall, 45 degrees to floor Structure above, and provide surface-applied cross bracing Above door between jamb-studs with typical wall framing studs. All security and STC 50 walls shall be painted from floor slab to deck above, fully tape and seal all seams, perimeter and all penetrations on both sides.
Reasor | 2026-05-11 | SOW p6, 3.1 references “true ceiling”, please clarify what constitutes a “true ceiling” in building 12. Will the existing roof assembly suffice? | Walls must go from floor slab (true floor) to underside of floor or roof deck (true ceiling). Reference UFC 4-010-05 Published 26 May 2023
Reasor | 2026-05-11 | Will STC-50 labeled doors be acceptable as far as STC requirements go? Note that door labels are lab-tested value, not a field-tested value. | Yes STC-50 Labeled Doors
Reasor | 2026-05-11 | SOW p8, 3.4 references “TEMPEST”. Will this 5000sf SCIF be a TEMPEST certified facility as stated in Design Review requirement in 3.6? | That is correct, the TEMPEST certified space boundary is shown in p5 with an orange boundary line (~5000sf). Level A
Reasor | 2026-05-11 | Will review meetings require attendance in-person at Eglin AFB, or on-line? | in-person attendance is preferred.
Reasor | 2026-05-11 | FPE Main Service SOW 3.4 requires removal/replacement of all FPE panels in the project area, fed from the MDP. Field observation indicates the existing MDP is itself an FPE panel. Please confirm whether replacement of this panel is within this scope. | Per SOW section 3.4 DESIGN ELEMENT FOUR – ELECTRICAL. That is correct, "The contractor shall remove or replace all FPE manufactured panels within project area to include the MDP.
Reasor | 2026-05-11 | Generator Fuel Type: Is natural gas available at the proposed generator location, or is diesel required? | Per UFC 3-540-01 - For the Air Force: Natural gas systems are not allowed. Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
Reasor | 2026-05-11 | Emergency Power Classification & Runtime Per SOW 3.8, confirm NEC classification (Article 700, 701, or 702) for the standby system and provide the required generator runtime / fuel tank sizing basis. Eglin Design Manual A14.3 item 14 establishes a 24-hour minimum for RPIE generators; please confirm whether 24 hours is the required basis or if a longer mission duration applies. | No longer mission duration required. Per Eglin Engineering Design Manual: RPIE generators will have a minimum 24-hour local capacity based on the actual generator load fuel consumption rate of the engine.
Reasor | 2026-05-11 | Rack Count Discrepancy SOW 3.1 indicates 30 racks; Attachment 5 (Bldg 12 Facilities Planning) indicates 20 racks. Please confirm the total rack count for design. | 30 racks
Reasor | 2026-05-11 | Server Room Heat Load SOW 3.1/3.2 specifies N+1 CRAC units but no load density. Please provide kW/rack (or total IT load) and confirm N+1 vs 2N intent for CRAC, PDU, and generator sizing. | Total IT Load: 800KW. CRAC: N+1 UPS/Batteries: Supply 800 KW to cover IT load Generator: Qty 1: 1 MW to cover IT Equipment and Chilled Water Plant & Cooling PDU: 2N (A and B Feeds). Each rack should have two independent PDUs (Feed A and Feed B), routed
Reasor | 2026-05-11 | Adjacent Project Drawings Can the Government provide electrical drawings for the adjacent SABER project currently under construction within Building 12? | Yes, there are 35% design drawings from the other 3 projects happening in the same facility.Attachments will include the design construction drawings.
Reasor | 2026-05-11 | TEMPEST Level SOW 3.6 requires a formal TEMPEST review. Please identify the assigned TEMPEST level. | Level A
Reasor | 2026-05-11 | Occupancy During Outage: Is Building 12 intended to remain occupied and under normal operation during utility power outages? | the limits within this project are intended to be operational during a power outage.
Reasor | 2026-05-11 | Generator Location and Site Civil Scope Please identify the assumed generator location, distance from the building, and confirm whether site civil work (concrete pad, bollards, fence/screening, underground feeder routing, trenching, restoration) is included in the base bid scope. | Diesel is the only Air Force approved Emergency Generator type A proposed location for the generator pad is in the green area between road and building on the north side. The contractor must finalize this location during the design phase to optimize feeder routing and ensure code compliance. Civil work, As the design builder the contractor is responsible for the comprehensive design and construction of all supporting civil elements. to include concrete pad, protective bollards, screening underground feeder routing, restoration etc. This will be included in the your proposal and is required to provide a complete and usable facility.
Reasor | 2026-05-11 | Drive Isolation Transformers for VFDs Eglin Design Manual requires drive isolation transformers for all VFDs. Confirm whether drive isolation transformers are required on this project. | Confirmed, that is correct IAW the most current version of the Eglin Design Guide
Reasor | 2026-05-11 | Will the server room be considered “incidental equipment” per ufc 3-600-01 and TSFPEWG-G-3-600-01-01-18? If not, what MAC category is the equipment? This will be needed to determine special fire protection requirements such as early warning smoke detection and clean agent fire suppression. | NIST 800-53 PE-13 server room must be considered mission critical.
Reasor | 2026-05-11 | The existing fire sprinkler appears to be original to the building. Will the sprinkler system remain and only be modified to suit the new floor plan and ceiling or will the sprinkler system in the area of work need to be replaced completely? | the intent is to modify the system to suit the new space. The request from the fire inspector is to replace the sprinkler heads and test the current/existing fire sprinkler system for the entire facility.
Reasor | 2026-05-11 | Will the existing fire alarm be replaced with fire alarm/mns in the other portion of the building currently under construction before this project is completed? | The exisiting fire alarm panel will be installed from another project, but all new fire alarms will either be tied into the main facility fire alarm panel, or be replaced on an isolated fire alarm panel.
Reasor | 2026-05-11 | Please confirm a new fire alarm/mass notification system will be required in the area of work. | Yes, the secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor.
Reasor | 2026-05-11 | Is the existing Monaco transceiver intended to remain and be reused, or be replaced? | The Monaco transceiver will be replaced by another project, however a new system will need to be installed for the secured area.
Reasor | 2026-05-11 | Per the plumbing site plan on Sheet C-3 dated 6/18/82, the service lateral serving the fire riser is 4 inches. If the fire sprinkler riser is being relocated, is it the Government’s intent to replace the entire service lateral with a new 6-inch or larger line back to the water main? | The secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. in accordance with the UFC 3-600-01 section 9-3.3.2 - "Minimum size Service Lateral for fire sprinkler systems must be not less than 6-in. (150 mm) in diameter." The fire riser will upsize to 6" and relocated (TBD) and a new 6" underground tap line from the water main to the fire riser is required.
Reasor | 2026-05-11 | Is fall protection required at the roof hatch and new roof-mounted equipment for this project? Please provide fall protection requirements for this project. | yes, railings at the roof hatch and a administrative control access zone with a visible line 10 ft from the edge of the roof or railing around entire perimeter of roof
Reasor | 2026-05-11 | Is cybersecurity required? If so, please provide the detailed cybersecurity requirements for the project. | YES. Cybersecurity is required for the information system inside the space. Collateral systems are managed under RMF using AFI 17-101 and NIST SP-800-53 rev5. SAP systems are managed under RMF using the Joint SAP Implementation Guide (JSIG) 2018 w/errata. Open office area & Data Lab (rms 12- 9) classification (TS/SCI, SAP) (NIST 800-53, CNSSI 1253, JSIG, IC Tech Spec - for ICD/ICS 705 domain-specific policies and procedures.)
Reasor | 2026-05-11 | Will the contractor be required to cover and protect any existing to-remain equipment, or will the user remove all existing equipment prior to construction? | The user is to move all equipment and vacate space prior construction start. There should be no equipment in the construction space.
Reasor | 2026-05-11 | What are the cooling requirements for the interior spaces? | Environmental control baselines required by NIST SP 800-53 PE-14 The contractor shall design and construct the interior IT space cooling systems to the following user requirements: The mechanical cooling system shall be sized to continuously cool a dedicated IT equipment load of 2.0 MW. The Computer Room Air Conditioning (CRAC) and chilled water infrastructure shall be designed and installed with N+1 redundancy. The Chilled Water Plant and all CRAC units must be connected to and supported by the 5.0 MW standby generator upon loss of utility power. Thermal Envelope (PE-14 Acceptable Levels): The facility must continuously maintain the interior IT spaces in accordance with ASHRAE TC 9.9 Class A1 and UFC 3-410-01 parameters: Temperature: 64.4°F to 80.6°F (18°C to 27°C) Dew Point: 41.9°F to 59.0°F (5.5°C to 15°C) Maximum Relative Humidity: 60%
Reasor | 2026-05-11 | What are the humidity requirements for the interior spaces? | NIST 800-53 PE-14
Reasor | 2026-05-11 | Please describe type of activity and room type/function of each room that requires HVAC in the scope of this project. This information will be used to optimize the HVAC equipment size and layout. Provide as much detail as possible. | The project consist of 3 major spaces Data server (SCIF) Open workoffice space. (SCIF) NEW restroom space. (Common space)
Reasor | 2026-05-11 | Can the users provide a list of heat producing equipment or the heat load for the interior spaces? | The total IT load is 800KW
Reasor | 2026-05-11 | Can the current facility users relocate during construction? Will any temporary facilities or cooling be required for the users? | portions of the building will be occupied by the user, however the boundaries within this project will be vacated during construction. NO temporary facility or cooling will be reqquired.
Reasor | 2026-05-11 | Will there be existing to remain building DDC to tie into? Or will new work be separate? | NEW DDC system will be required to tie to the existing Eglin AFB BACnet.
Reasor | 2026-05-11 | What is the state of the existing Energy Management Controls System (EMCS)? Any existing drawings or controls diagrams of the existing EMCS? | As-built drawings will be provided. Please refer to Eglin Design Guide dated March 2025 section A11.1.3.1
Reasor | 2026-05-11 | In the RFP Attachment 5, Diagram 2, there is a long thin space to the plan west of Room 7. What is the purpose of this space? | In accordance with the TEMPEST Room Diagram Template, this space is configured to house a GSA-approved secure safe and multi-function printers.
Reasor | 2026-05-11 | In the RFP Attachment 5, Diagram 2, there is a red line defining the complete perimeter. Is this the ICD705 secure perimeter? Are there no secure compartments within this secure perimeter? | This is the ICD705 Perimeter but all partitions and compartmented rooms inside the red defined perimeter must have Wall Type A and STC-50 rated doors.
Reasor | 2026-05-11 | The RFP SOW, p2 Existing Building Conditions states there is an ACM Survey dated 12/13/24, can this be provided? | Per the ACM Survey dated 12/13/24. hazmat has been found and abated on certain areas of the building. This survey does not show any samples within the specific project footprint. Therefore, the contractor must include the cost of localized pre-demolition testing in their proposal. To ensure a fair bidding environment for the abatement (removal) portion, all bidders shall include a fixed allowance of $25,000 in their proposal for potential ACM abatement. If ACM is discovered during testing, it will be paid out of this allowance based on actual verified costs. If no ACM is found, the unused allowance funds will be returned to the Government.
Reasor | 2026-05-11 | The RFP SOW requires 18” raised access floor in the server room, is there a waiver for handicap-access? Or will an 18’ ramp will be required. | the ramp is required. However, the minimum height for the finished floor will be determined by the design, considering space for cabling and hvac .
Reasor | 2026-05-11 | Is there a basis of design to use for Bid Option 001 FF&E? | there is a layout plan and user space intention but a full interior design plan is required as part of this task.
Reasor | 2026-05-11 | Will any fall protection need to be design and constructed around the new RTU and roof hatch? If so, to what extent? | yes, railings at the roof hatch and a administrative control access zone with a visible line 10 ft from the edge of the roof or railing around entire perimeter of roof
Brawley | 2026-05-11 | There is mention of a 100P corrected submittal in one spot. Should we expect to provide 5 submittals: 35P, 65P, 95P, 100P, and corrected 100P? | To maximize the efficiency of this Design-Build project while adhering to strict ICD 705 SCIF accreditation requirements, the government is tailoring the submittal schedule. The contractor shall provide 35%, 95%, and Final (100% CF) design submittals. The 95% submittal is strictly required to verify critical SCIF acoustic and physical security details prior to the issuance of the Final construction documents.
Brawley | 2026-05-11 | Are there any security requirements for the restrooms to be located outside of the secure area? | no secure requirements, the restroom must be accesible to all building personnel.
Brawley | 2026-05-11 | Are the sanitary sewer drain and domestic water supply lines anticipated to be able to be reused? If they are not, is a change order expected? | Based on the conditions of the existing sanitary sewr system, it Is required to replaced the entire kitchen sewer system to include grease traps and piping, potentially cap and abandone in place, and install new sewer system piping to suit the new restroom space needs all the way to the gravity main service line.
Brawley | 2026-05-11 | Request the government waive the requirement for hard copies. | Design submital hard copies required.
Brawley | 2026-05-11 | Request the government waive the requirement for CDs. | Design submital CDs required.
Brawley | 2026-05-11 | Does Bid Option 001 include design or construction only? | per the SOW - section 3.7 Design element Seven is to provide FURNITURE, FIXTURE & EQUIPMENT (FF&E) Plan. "The contractor shall provide all professional services and coordination required to develop a comprehensive, non-proprietary FF&E Procurement Data Package." section 3.7.1 - BID OPTION 001 – FF&E ASSEMBLY AND INSTALLATION. "Provide services to include furniture purchase, field measuring, installation drawings, shipping and delivery coordination, receiving, inspection, submitting and processing freight and warranty claims, unpacking, storing, assembly, installation and other related activities or tasks for a complete and functional installation. "
Brawley | 2026-05-11 | Should any additional design documents be included with the bid submission? | the government will provide as builds and 35% drawings from the saber project going on.
Brawley | 2026-05-11 | What are the extents of the existing construction contract within the building seen during site visit? | Please refer to the SOW p5 Figure 3. Proposed area: ICD 705 office workspace, server room, and restroom area.
Brawley | 2026-05-11 | Will this contract only be responsible for the construction of the SCIF and restroom? | That is correct. Project consist of (2) areas (a) new SCIF to include a Secure Office workspace, and (b) Secure server Room. The scond area will be the Restroom outside of the Secure perimeter.
Brawley | 2026-05-11 | Is the restroom area required to be ICD 705 compliant, or only the SCIF footprint? | There are no restrooms planned for the ICD-705 build. All restrooms planned are outside that area.
Brawley | 2026-05-11 | Provide the final preliminary concept floor plan, scaled CAD/PDF, and room data sheet. | the user TEMPEST room space Diagram will be proivded.
Brawley | 2026-05-11 | Define IDS/ACS scope: pathways only or complete installed/tested systems? | per SOW section 3.5 - Security "contarctor responsible to provide infrastructure pathways for the IDS and ACS systems." no wiring or equipment is required.
Brawley | 2026-05-11 | Define UPS scope: GFE only, contractor rough-in only, or full UPS installation? | per SOW section 3.4 - ELECTRICAL "The design shall provide all required infrastructure, including dedicated conduit pathways and transfer switch tie-in points, to support a future Government-Furnished Uninterruptible Power Supply (UPS) system."
Brawley | 2026-05-11 | Provide generator runtime, preferred location, available utility routing, and AFCEC approval responsibility. | No longer mission duration required. Per Eglin Engineering Design Manual: RPIE generators will have a minimum 24-hour local capacity based on the actual generator load fuel consumption rate of the engine.
Brawley | 2026-05-11 | Confirm fire alarm, mass notification, sprinkler, and fire-protection modifications. | Yes, the secured area will need to be on a separate alarm/mass notification system. However areas outside of the secured area will need to be tied into the new alarm panel that will be installed by another contractor. Sprinkler system is to be modified to suit the new floorplan. the fire riser must be re-located in accordance with UFC 3-600-01.
Brawley | 2026-05-11 | Provide existing structural drawings or confirm contractor must perform structural investigation. | as build to be provided.
Brawley | 2026-05-11 | Confirm whether hazmat abatement is base bid, allowance, or post-survey modification. | Per the ACM Survey dated 12/13/24. hazmat has been found and abated on certain areas of the building. This survey does not show any samples within the specific project footprint. Therefore, the contractor must include the cost of localized pre-demolition testing in their proposal. To ensure a fair bidding environment for the abatement (removal) portion, all bidders shall include a fixed allowance of $25,000 in their proposal for potential ACM abatement. If ACM is discovered during testing, it will be paid out of this allowance based on actual verified costs. If no ACM is found, the unused allowance funds will be returned to the Government.