## RFI Submission Form
Pre-Proposal RFIs
Submitted By | Date Submitted | Inquiry | Government Response
OAC Action Construction Corp | 2026-06-05 | Please confirm that the specified IT heat load is 800 kW. Based on our preliminary analysis, supporting an 800 kW load with the required redundancy appears to require approximately 315 tons of cooling capacity, multiple CRAC units, and significantly larger chilled water infrastructure than currently depicted. Please confirm that the 800 kW heat load is correct. | CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. Per UFC 3-501-01, Section 3-2.3, the Contractor must complete a preliminary Load Analysis. The 'Raw Connected Load' for the 25 server racks is established at 700 kW based on the conceptual IT equipment list. However, this is only the connected baseline "it shall not be used as the mechanical design load". Per UFC 3-501-01, Appendix C (C-1.3.1), the Contractor must apply a Demand/Diversity Factor to transition from 'Connected Load' to 'Design Demand Load'. Sizing calculations must reflect the tailored 5-rack network configuration and apply an operational demand factor (at 80% peak factor). Per UFC 3-410-01, Cooling systems must be sized using the 'Block Load' method under ASHRAE Standard 183 guidelines. "Sizing must be strictly based on the system Peak load" UFC 3-410-01 explicitly mandates: 'Do not oversize the system. Do not add safety factors in the load calculations.
OAC Action Construction Corp | 2026-06-05 | Based on the specified 800 kW IT load, N+1 cooling redundancy requirements, and the target server rack count, the current server room appears insufficient to accommodate the required CRAC units, server racks, and maintenance clearances. Please provide direction regarding the required server room size and whether expansion of the server room is anticipated. | No server room expansion is anticipated at this time, the current server room foot print is sufficient. The contractor must demonstrate in their proposal that the optimized cooling layout (using the corrected 488 kW load) fits comfortably within the specified server room envelope while meeting all standard National Electrical Code (NEC) and manufacturer maintenance clearances.
OAC Action Construction Corp | 2026-06-05 | Please identify the Government's preferred location for the chillers and associated cooling equipment, or confirm that equipment locations are to be determined by the Contractor during the design phase. | potential location for a mechanical yard could be by the electrical room on the southwest side of the building. Can be discussed and finalize during design phase.
OAC Action Construction Corp | 2026-06-05 | Given the significance of the outstanding technical questions and their impact on the mechanical system design, will the Government consider extending the proposal due date until responses to these RFIs have been provided? | Yes
Onopa | 2026-06-05 | Verify the required server room cooling load (currently understood to be 800 kW). | CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. Per UFC 3-501-01, Section 3-2.3, the Contractor must complete a preliminary Load Analysis. The 'Raw Connected Load' for the 25 server racks is established at 700 kW based on the conceptual IT equipment list. However, this is only the connected baseline "it shall not be used as the mechanical design load". Per UFC 3-501-01, Appendix C (C-1.3.1), the Contractor must apply a Demand/Diversity Factor to transition from 'Connected Load' to 'Design Demand Load'. Sizing calculations must reflect the tailored 5-rack network configuration and apply an operational demand factor (at 80% peak factor). Per UFC 3-410-01, Cooling systems must be sized using the 'Block Load' method under ASHRAE Standard 183 guidelines. "Sizing must be strictly based on the system Peak load" UFC 3-410-01 explicitly mandates: 'Do not oversize the system. Do not add safety factors in the load calculations.
Onopa | 2026-06-05 | Confirm that the server room size shown on the contract documents is sufficient to accommodate the required cooling equipment and associated server rack layouts necessary to support the design load. | No server room expansion is anticipated at this time, the current server room foot print is sufficient. The contractor must demonstrate in their proposal that the optimized cooling layout (using the corrected 488 kW load) fits comfortably within the specified server room envelope while meeting all standard National Electrical Code (NEC) and manufacturer maintenance clearances.
Onopa | 2026-06-05 | Identify the intended location and applicable design requirements for the associated chiller equipment. | potential location for a mechanical yard could be by the electrical room on the southwest side of the building. Can be discussed and finalize during design phase.
Onopa | 2026-06-05 | Identify the intended location and applicable design requirements for the associated chiller equipment. | potential location for a mechanical yard could be by the electrical room on the southwest side of the building. Can be discussed and finalize during design phase.
Onopa | 2026-06-05 | Identify the intended location and applicable design requirements for the associated chiller equipment. | potential location for a mechanical yard could be by the electrical room on the southwest side of the building. Can be discussed and finalize during design phase.
Rogue and Sourza | 2026-06-05 | The RFI responses and updated SOW dated June 2, 2026 have generated more questions. Included is a list of questions we have for the mechanical, but please keep in mind we’re still reviewing the RFI responses. 800kW heat load equals 227 Tons of sensible cooling. The Liebert CRAC units can handle roughly 80% Sensible Heat Ratio so the total cooling needed will be 285 nominal Tons. 10% Safety Factor gives 315 nominal Tons. | CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. Per UFC 3-501-01, Section 3-2.3, the Contractor must complete a preliminary Load Analysis. The 'Raw Connected Load' for the 25 server racks is established at 700 kW based on the conceptual IT equipment list. However, this is only the connected baseline "it shall not be used as the mechanical design load". Per UFC 3-501-01, Appendix C (C-1.3.1), the Contractor must apply a Demand/Diversity Factor to transition from 'Connected Load' to 'Design Demand Load'. Sizing calculations must reflect the tailored 5-rack network configuration and apply an operational demand factor (at 80% peak factor). Per UFC 3-410-01, Cooling systems must be sized using the 'Block Load' method under ASHRAE Standard 183 guidelines. "Sizing must be strictly based on the system Peak load" UFC 3-410-01 explicitly mandates: 'Do not oversize the system. Do not add safety factors in the load calculations.
Rogue and Sourza | 2026-06-05 | The largest chilled water Liebert CRAC unit does 60 nominal Tons of cooling, so we’d need 6 of those units plus 1 for N+1 redundancy. We’ll also need two 315 Ton chillers to meet redundancy requirements. | CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. Per UFC 3-501-01, Section 3-2.3, the Contractor must complete a preliminary Load Analysis. The 'Raw Connected Load' for the 25 server racks is established at 700 kW based on the conceptual IT equipment list. However, this is only the connected baseline "it shall not be used as the mechanical design load". Per UFC 3-501-01, Appendix C (C-1.3.1), the Contractor must apply a Demand/Diversity Factor to transition from 'Connected Load' to 'Design Demand Load'. Sizing calculations must reflect the tailored 5-rack network configuration and apply an operational demand factor (at 80% peak factor). Per UFC 3-410-01, Cooling systems must be sized using the 'Block Load' method under ASHRAE Standard 183 guidelines. "Sizing must be strictly based on the system Peak load" UFC 3-410-01 explicitly mandates: 'Do not oversize the system. Do not add safety factors in the load calculations.
Rogue and Sourza | 2026-06-05 | CRAC unit size : approx. 10’ wide by 3.5’ wide by 8’ tall each Chiller size: approx. 38’long by 8’ wide by 9’ tall (each) Attached pdf shows the CRAC units in the server room, and the chiller size to scale. • Please request a verification of the load (800kW). • Size of server room is insufficient to fit required CRAC units and server racks. Please request direction for server room size. • Please request preferred location for chillers | CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. no server room expansion is anticipated, potential location for a mechanical yard could be by the electrical room on the southwest side of the building. Can be discussed and finalize during design phase.
Brawley | 2026-06-08 | What is the true IT Load? | What is the true IT Load? - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW.
Brawley | 2026-06-08 | What is the true generator sizing capacity? | – the generator shall be size to maintain continuous power in case of an outage to the server room equipment and the server rm HVAC. The capacity of the generator will be determined by the design.
Reasor | 2026-06-10 | After reviewing the RFI responses with our DOR and subcontractors, we have two additional RFIs that we would like to submit that concerns the constructability of the mechanical scope and the workstation requirement, and would appreciate if you could address this: 1. Based on line 19 of the RFI Responses, the government has stated that an 800kW IT heat load will be required to be cooled. Our engineer has calculated that ~7 40-ton CRAC units will need to be installed in the server room in order to meet this demand. With the size of these units, and the size of the ~20 server racks that are to be installed in this room, the room size is vastly too small. Due to the size requirements of these units, mechanical contractors are unable to provide accurate pricing for this project. a. Can you please clarify the scope to lower the IT load requirement of the server room? (Recommended) b. Can you please clarify the scope to allow for a larger server room? (This option will reduce the usable office space, and will impact the space required to house the total occupant count of 30 workstations stated in the SOW) 2. Based on preliminary design of the FF&E workstations with the DOR & Furniture subcontractor for the SWD/SWT Room, there is not sufficient space within the allotted area to install workstations for (37) personnel. Based on the most economical layout we can use, there is space for (27) workstations to be installed given current space requirements. a. Please confirm if the SOW can be updated to reduce the required number of personnel in the SWD/SWT Room? | CENPM – the user has provided equipment information the total IT load has been revised. “CEN ,PM - The type of HVAC system for the server room shall be determined during the Design phase of this project. The Contractor shall evaluate both Computer Room Air Conditioning (CRAC) units (perimeter cooling) and In-Row cooling systems. The final selection shall be justified through a comprehensive engineering trade-off and Life-Cycle Cost Analysis (LCCA) submitted with the 35% Design Deliverable, demonstrating compliance with UFC 3-410-01 (HVAC Systems), UFC 3-580-01 (Telecommunications Building Cabling Systems), and ASHRAE TC 9.9. Connected IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW. Per UFC 3-501-01, Section 3-2.3, the Contractor must complete a preliminary Load Analysis. The 'Raw Connected Load' for the 25 server racks is established at 700 kW based on the conceptual IT equipment list. However, this is only the connected baseline "it shall not be used as the mechanical design load". Per UFC 3-501-01, Appendix C (C-1.3.1), the Contractor must apply a Demand/Diversity Factor to transition from 'Connected Load' to 'Design Demand Load'. Sizing calculations must reflect the tailored 5-rack network configuration and apply an operational demand factor (at 80% peak factor). Per UFC 3-410-01, Cooling systems must be sized using the 'Block Load' method under ASHRAE Standard 183 guidelines. "Sizing must be strictly based on the system Peak load" UFC 3-410-01 explicitly mandates: 'Do not oversize the system. Do not add safety factors in the load calculations.” CENPM No server room expansion is anticipated at this time, the current server room foot print is sufficient. The space intent “diagram” provided by the user could be modified but needs to be in coordination and approved by the user at the design phase. I am not sure what SWD/SWT room is. However, the contractor must go with the requirement in SOW. Any other detail will be defined at the design.
OK2 | 2026-06-10 | Generator Sizing Flag: The preliminary standby demand is approx. 1,355 kW against the Govt-directed 1 MW generator (136% loaded). Floor space is a concern: in addition to the 20-30 racks, the room must house the (7) 60-ton CRAC units, (4) 500 kVA floor PDUs, future GFE UPS-A/UPS-B pads, iso xfmrs, and associated distribution equipment, and the preliminary layout indicates insufficient area to fit all equipment w/ required working clearances and service access. Coordinate equipment placement across all trades and confirm the final room footprint w/ the Govt early in design. Wireless access points are assumed not allowed within the secure area unless approved by the Govt and the accrediting authority • IT load RFI discrepancy: The SOW and most RFI responses state an 800 kW IT load and a 1 MW generator; two cooling RFI responses state a 2.0 MW IT cooling load and a 5.0 MW generator. Confirm 800 kW is the intended design-basis IT load. • Generator sizing: Even at the 800 kW IT load basis, the preliminary standby demand (approx. 1,355 kW) exceeds the Govt-directed 1 MW generator at 136% loading. Carry as a bid qualification; final rating to be validated with Gen Size per UFC 3-504-01 at the 35% design. • Inside-plant fiber scope: Confirm inside-plant fiber counts, types, termination, and testing responsibility. • Rack count (informational): Per the Govt RFI response, 30 racks are the objective, and 20 racks is the min threshold (7 ft racks). Rack, rack PDU (2 per rack), ladder rack, and cabling quantities scale w/ the final count - confirm the design-basis rack count. Commissioning: The SOW requires system commissioning only for the HVAC scope (SOW 3.2) and is silent on a third-party CxA or commissioning of the electrical and telecom systems. A project of this scale (chilled water plant, CRAC units, DDC/EMCS integration, generator, and ATS) typically triggers total building commissioning per UFC 1-200-02 - confirm via RFI whether a CxA and electrical/telecom commissioning are required, and carry as a bid qualification | The generator must be size to cover the mission critical equipment at the server room and its cooling system. “We have been coordinating with 96 CS to have a 48 Strand Core Fiber run into Bldg 12 Rm 1003 that should take place prior to this effort starting construction. We have also started conversations with 96 CS on how we then run fiber from Rm 1003 to the Co-Use/Server Room spaces. Some coordination with 96 CS will need to be completed as part of the design for bringing in the fiber.” “We have been coordinating with 96 CS to have a 48 Strand Core Fiber run into Bldg 12 Rm 1003 that should take place prior to this effort starting construction. We have also started conversations with 96 CS on how we then run fiber from Rm 1003 to the Co-Use/Server Room spaces. Some coordination with 96 CS will need to be completed as part of the design for bringing in the fiber.” Total IT Load: IT load: 4 x 1-U switch @ 3.4 kW 7 x 2-U hypervisor servers @ 12.6 kW 5 x 4-U NetApp filers @ 12 kW 1 Rack @ 28kw * 20 = 560kW Additionally, 5 network racks are going to be tailored for enterprise network switches at less power consumption ~ 10 kW a piece (totaling 50kW). Total power IT load 610kW.